## Building A
Building A — Lighting Place Schedule
Floor | Room No. | Place | Task / Area Type | Workplane Height (m) | Target Maintained lx | Initial Target lx (MF 0.8) | g1 Uniformity Target | Glare / Design Notes | AS/NZS 1680 Reference | Measurement Note | Existing Luminaire | Existing Qty | Existing W each | Existing Total W | Proposed Luminaire | Proposed Qty | Proposed W each | Proposed Total W | Estimated Saving W | Status
Ground | 101 | Stairs | Stairs / circulation | 0 | 80 | 100 | ≥ 0.3 along route | Control glare; light stair treads evenly | AS/NZS 1680.2.1 internal stairs | Measure on stair tread/floor path | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 102 | Corridor / Lobby | Corridor / passageway / lobby | 0 | 40 | 50 | ≥ 0.3 along route | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 103 | Toilet | Toilet / amenities | 0 | 160 | 200 | ≥ 0.3–0.5 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 104 | Toilet | Toilet / amenities | 0 | 160 | 200 | ≥ 0.3–0.5 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 105 | Toilet Disabled | Toilet / accessible amenities | 0 | 160 | 200 | ≥ 0.3–0.5 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 106 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 107 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 108 | Corridor | Corridor / passageway | 0 | 40 | 50 | ≥ 0.3 along route | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 109 | Mail | Office / mail task area | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 110 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 111 | CAD | CAD / screen-based office work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 112 | CAD | CAD / screen-based office work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 113 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 114 | Visitors | Office / visitors / meeting | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 201A | Stairs | Stairs / circulation | 0 | 80 | 100 | ≥ 0.3 along route | Control glare; light stair treads evenly | AS/NZS 1680.2.1 internal stairs | Measure on stair tread/floor path | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 202 | Corridor | Corridor / passageway | 0 | 40 | 50 | ≥ 0.3 along route | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 203 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 204 | Manager | Manager office | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 205 | Balcony | Balcony / circulation | 0 | 40 | 50 | ≥ 0.3 along route | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 206 | Toilet | Toilet / amenities | 0 | 160 | 200 | ≥ 0.3–0.5 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 207 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 208 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 209 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 210 | CAD | CAD / screen-based office work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 211 | Corridor | Corridor / passageway | 0 | 40 | 50 | ≥ 0.3 along route | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 212 | Common | Common office / collaboration | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 213 | Balcony | Balcony / circulation | 0 | 40 | 50 | ≥ 0.3 along route | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 214 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 215 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 216 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 217 | Toilet | Toilet / amenities | 0 | 160 | 200 | ≥ 0.3–0.5 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 218 | Toilet | Toilet / amenities | 0 | 160 | 200 | ≥ 0.3–0.5 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 219 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 220 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed

## Building B
Building B — Lighting Place Schedule
Floor | Room No. | Place | Task / Area Type | Workplane Height (m) | Target Maintained lx | Initial Target lx (MF 0.8) | g1 Uniformity Target | Glare / Design Notes | AS/NZS 1680 Reference | Measurement Note | Existing Luminaire | Existing Qty | Existing W each | Existing Total W | Proposed Luminaire | Proposed Qty | Proposed W each | Proposed Total W | Estimated Saving W | Status
Ground | 101 | Stairs | Stairs / circulation | 0 | 80 | 100 | ≥ 0.3 along route | Control glare; light stair treads evenly | AS/NZS 1680.2.1 internal stairs | Measure on stair tread/floor path | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 102 | Corridor | Corridor / passageway | 0 | 40 | 50 | ≥ 0.3 along route | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 103 | Storage | Storage / occasional use | 0 | 80 | 100 | ≥ 0.3–0.5 | Enough light for safe access | AS/NZS 1680.2.1 comparable storage/movement | Use 40 lx only if rarely entered; 80 lx safer | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 104 | Utility | Utility / cleaner room | 0 | 80 | 100 | ≥ 0.3–0.5 | Avoid glare; allow safe use of equipment | AS/NZS 1680.2.1 comparable utility area | Use 0.7 m if detailed work is done | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 105 | WC | Toilet / amenities | 0 | 160 | 200 | ≥ 0.3–0.5 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 106 | WC | Toilet / amenities | 0 | 160 | 200 | ≥ 0.3–0.5 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 107 | Shower | Shower / amenities | 0 | 160 | 200 | ≥ 0.3–0.5 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 108 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 110 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 111 | Manager | Manager office | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 112 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 113 | Corridor / Coffee | Corridor / coffee area | 0 | 40 | 50 | ≥ 0.3 along route | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 114 | Storage | Storage / occasional use | 0 | 80 | 100 | ≥ 0.3–0.5 | Enough light for safe access | AS/NZS 1680.2.1 comparable storage/movement | Use 40 lx only if rarely entered; 80 lx safer | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 115 | Reception | Reception / enquiry desk | 0.7 | 320 | 400 | ≥ 0.7 on task area | Good facial visibility; low glare | AS/NZS 1680.1 enquiry desks / office tasks | Desk/counter task plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 116 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 117 | Corridor | Corridor / passageway | 0 | 40 | 50 | ≥ 0.3 along route | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 118 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 119 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 120 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 121 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 201 | Stairs | Stairs / circulation | 0 | 80 | 100 | ≥ 0.3 along route | Control glare; light stair treads evenly | AS/NZS 1680.2.1 internal stairs | Measure on stair tread/floor path | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 203A | DB | Electrical DB / utility | 0 | 80 | 100 | ≥ 0.3–0.5 | Avoid glare; allow safe use of equipment | AS/NZS 1680.2.1 comparable utility area | Use 0.7 m if detailed work is done | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 203 | Director | Director office | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 204 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 205 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 206 | Kitchen | Kitchen / kitchenette | 0.85 | 160 | 200 | ≥ 0.5 | Good bench visibility; avoid glare | AS/NZS 1680.2.1 kitchen general | Use 240 lx at food prep/washing-up benches | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 207 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 208 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 209 | Toilet | Toilet / amenities | 0 | 160 | 200 | ≥ 0.3–0.5 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 210 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 211 | Toilet | Toilet / amenities | 0 | 160 | 200 | ≥ 0.3–0.5 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 212 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed
First | 212A | DB | Electrical DB / utility | 0 | 80 | 100 | ≥ 0.3–0.5 | Avoid glare; allow safe use of equipment | AS/NZS 1680.2.1 comparable utility area | Use 0.7 m if detailed work is done | Batten 2 × 36W |  | 72 |  | LED batten / linear |  |  |  |  | To be assessed
First | 213 | Conference | Conference room | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Troffer 4 × 36W |  | 144 |  | LED low-glare panel |  |  |  |  | To be assessed

## Reference
AS/NZS 1680 quick reference used in schedules
Space / task | Workplane height (m) | Maintained lux | Initial lux target (MF 0.8) | g1 uniformity | Glare note | Reference basis | Measurement note
Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare / UGR ≤19 preferred; control screen reflections | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height plane
Meeting / conference | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow dimming for presentation | AS/NZS 1680.1 comparable office task | Table-height plane
Reception / enquiry desk | 0.7 | 320 | 400 | ≥ 0.7 on task area | Good facial visibility; low glare | AS/NZS 1680.1 enquiry desks | Counter/desk plane
Corridor / passageway | 0 | 40 | 50 | ≥ 0.3 along route | Avoid dark patches and glare | AS/NZS 1680.2.1 circulation | Floor level
Stairs | 0 | 80 | 100 | ≥ 0.3 along route | Light treads evenly | AS/NZS 1680.2.1 internal stairs | Stair tread/floor path
Storage / occasional use | 0 | 80 | 100 | ≥ 0.3–0.5 | Safe access lighting | AS/NZS 1680.2.1 comparable storage | Floor level
Utility / DB | 0 | 80 | 100 | ≥ 0.3–0.5 | Safe equipment access | AS/NZS 1680 comparable utility | Use actual task plane if needed
Toilet / WC / shower | 0 | 160 | 200 | ≥ 0.3–0.5 | Comfortable general lighting; IP-rated in wet areas | AS/NZS 1680 comparable amenities | Floor level
Kitchen general | 0.85 | 160 | 200 | ≥ 0.5 | Bench visibility | AS/NZS 1680.2.1 kitchen general | Bench height
Food prep / washing up | 0.85 | 240 | 300 | ≥ 0.7 on task area | Control glare on wet surfaces | AS/NZS 1680.2.1 food preparation | Bench height