## Summary
Emergency Lighting Requirement & Room-by-Room Take-off – Building A and B
Prepared 2026-05-19 ¦ Based on AS/NZS 2293 series and NZBC F6/F8 references.
Important limitation | I do not have the actual floor plans / confirmed room list in this chat. So the Building A/B tabs are a detailed editable take-off template with example room numbers. Replace the room numbers/area data with the real plan room numbers and the formulas will update counts.
Main design standard | AS/NZS 2293.1:2018 + Amendment 1:2021 — system design, installation and operation
Luminaire product standard | AS/NZS 2293.3:2018 + Amendment 1:2021 — emergency luminaires and exit signs
Maintenance standard | AS/NZS 2293.2:2019 — routine service and maintenance
Emergency duration | In-service emergency operation: 90 min unless NZBC/building regulation specifies otherwise. Initial commissioning test: 1.33 × required duration.
Design illuminance | General designated areas are checked using AS/NZS 2293.1 spacing/calc method; stairways require 1 lx on landings and treads.
Maximum area per fitting | A single emergency luminaire shall not serve more than 500 m².
Exit signs | Required locations are determined by NZBC F8/AS1; signs must conform to AS/NZS 2293.3 and be visible for the designed viewing distance.
How to use | Enter real room/area numbers, area, number of exit-sign doorways, corridor intersections, direction changes, level changes, and stair points. Use 'Proposed' columns for your actual design.
Workbook sheets | Purpose
Requirements | Detailed rule/checklist from AS/NZS 2293.1, 2293.2 and 2293.3.
Building A | Room-by-room/area-by-area take-off worksheet for Building A.
Building B | Room-by-room/area-by-area take-off worksheet for Building B.
Take-off Summary | Auto-summarises total required/proposed emergency lights and exit signs.
Maintenance | Service and maintenance checklist.
References | Source standards and clauses used.

## Requirements
Emergency lighting and exit sign requirements checklist
Item | Requirement / rule | Design implication | Required value / action | Applies to | Standard reference | Check status
1 | Emergency luminaires shall be installed throughout the designated area. | All escape routes/designated spaces in Building A and B need emergency coverage. | Provide emergency luminaires in every designated escape area. | Both | AS/NZS 2293.1:2018 Cl 4.3 | To check
2 | One emergency luminaire must not serve an area larger than 500 m². | Large open areas need more than one fitting even before spacing/calculation checks. | Minimum area allowance = CEILING(area/500). | Both | AS/NZS 2293.1:2018 Cl 4.3 | To check
3 | Emergency luminaire required within 2 m on the approach side of each doorway requiring an exit sign. | Count exit-sign doors; each normally triggers a nearby emergency luminaire unless a compliant dual-function sign covers it. | Within 2 m of approach side. | Both | AS/NZS 2293.1:2018 Cl 4.5 | To check
4 | Emergency luminaire required within 2 m of corridor intersections. | Count T/intersection points in corridors. | Within 2 m of centre-line intersection. | Both | AS/NZS 2293.1:2018 Cl 4.5(a) | To check
5 | Emergency luminaire required within 2 m of changes in direction, unless the straight-line/spacing exception applies. | Count corridor bends/turns; designer may justify omission only if exception is satisfied. | Within 2 m of direction change. | Both | AS/NZS 2293.1:2018 Cl 4.5(b) | To check
6 | Emergency luminaire required within 2 m of any change of floor level, on the low side. | Count ramps, steps, level transitions. | Within 2 m on low side. | Both | AS/NZS 2293.1:2018 Cl 4.5(c) | To check
7 | Stairways require emergency luminaires installed in accordance with stairway rules. | Do a dedicated stair calculation using 1 lx tables/calculation; do not rely on normal corridor spacing only. | 1 lx on each landing and tread surface. | Stairs | AS/NZS 2293.1:2018 Cl 4.8.3/4.8.4 | To check
8 | For direct lighting, use spacing rules or illuminance calculations. | Final number depends on luminaire classification, mounting height, spacing table and layout. | Appendix E: 0.2 lx; Appendix F: 1 lx for stairs. | Both | AS/NZS 2293.1:2018 Cl 4.6, App E/F | To check
9 | Maintained/combined maintained emergency luminaires on stairs need de-rating to next higher classification. | When using maintained or combined maintained fittings on stairs, select next higher classification in Appendix F. | Use next higher classification. | Stairs | AS/NZS 2293.1 Amd 1:2021 Cl 4.8.2 | To check
10 | Exit signs shall be installed where required by NZBC F8/AS1 and conform to AS/NZS 2293.3. | Provide exit/directional signs at required exits and where direction is not obvious. | Use correct sign type and viewing distance. | Both | AS/NZS 2293.1:2018 Cl 5.2; AS/NZS 2293.3 | To check
11 | Exit signs should normally be mounted 2.0 m to 2.7 m above floor level; if not practical, consider larger sign size. | Confirm mounting height on drawings. | 2.0–2.7 m typical mounting range. | Both | AS/NZS 2293.1:2018 Cl 5.8 | To check
12 | Emergency luminaires and exit signs must operate on loss of normal lighting supply in the designated area. | Sensing/control wiring must be connected to relevant normal lighting subcircuits. | Automatic operation on supply failure. | Both | AS/NZS 2293.1:2018 Cl 2.3.3 | To check
13 | Every emergency luminaire/exit sign must be uniquely identifiable for inspection and maintenance. | Assign IDs such as A-EL-001, A-EX-001, B-EL-001. | Unique visible identifier. | Both | AS/NZS 2293.1:2018 Cl 2.5 | To check
14 | A dual-function internally illuminated exit sign may count as both exit sign and emergency luminaire if it meets both requirements. | Can reduce fitting count near exits, but only if product data/classification supports it. | Must comply with both emergency luminaire and exit sign requirements. | Both | AS/NZS 2293.1:2018 Cl 4.4 | To check
15 | Self-contained emergency luminaires/exit signs require battery charger indication and test facilities. | Select products with visible charge indicator and discharge test facility. | Indicator visible; test without disconnecting normal lighting. | Both | AS/NZS 2293.1:2018 Section 3; AS/NZS 2293.3 Cl 4.4 | To check
16 | Routine service records must include installed fittings, quantity/type/location, defects, responsible entity and service details. | Keep an emergency light schedule as baseline/maintenance data. | Retain records for 7 years. | Both | AS/NZS 2293.2:2019 Cl 2.7 | To check

## Building A
Building A – emergency lighting room/area take-off
Replace example room numbers/areas with the actual plan. Formula is a conservative planning estimate; final design must be verified against AS/NZS 2293.1 spacing tables or illuminance calculation.
Building | Level | Room/Area No. | Room/Area name | Area type | Area m² | Exit-sign doorways | Corridor intersections | Direction changes | Floor level changes | Stair/landing points requiring calc | Spacing/calc extra lights | Dual-function exit sign used? | Min emergency lights by formula | Proposed emergency lights | Exit signs required | Proposed exit signs | Fitting IDs / labels | Mounting / location notes | Compliance status | Designer notes
A | G | A-001 | Main entrance / lobby | Lobby | 120 | 2 | 0 | 0 | 0 | 0 | 0 | No | 2 | 2 | 2 | 2 |  | Exit sign at each required exit door. EM within 2 m approach side. | To check | Update with real plan room number.
A | G | A-002 | Main corridor | Corridor | 90 | 0 | 2 | 1 | 0 | 0 | 0 | No | 3 | 3 | 0 | 0 |  | EM within 2 m of intersections and direction changes; check spacing table between fittings. | To check
A | G | A-003 | Stair 1 | Stair | 35 | 1 | 0 | 0 | 0 | 4 | 0 | No | 5 | 5 | 1 | 1 |  | Use 1 lx Appendix F / calculation for each landing and tread. Position to avoid glare. | To check
A | G | A-004 | Stair 2 | Stair | 35 | 1 | 0 | 0 | 0 | 4 | 0 | No | 5 | 5 | 1 | 1 |  | Use 1 lx Appendix F / calculation for each landing and tread. Position to avoid glare. | To check
A | G | A-005 | Open office / work area | Office | 320 | 0 | 0 | 0 | 0 | 0 | 1 | No | 1 | 1 | 0 | 0 |  | At least by area allowance; add fittings using spacing table for selected classification. | To check
A | G | A-006 | Plant / switchboard room | Plant room | 60 | 0 | 0 | 0 | 0 | 0 | 0 | No | 1 | 1 | 0 | 0 |  | Provide emergency lighting if part of designated route or required by fire/maintenance strategy. | To check
A | G | A-007 | Toilets / amenities | Toilets | 45 | 0 | 0 | 0 | 0 | 0 | 0 | No | 1 | 1 | 0 | 0 |  | Emergency coverage needed if designated area or internal path of travel. | To check
A | G | A-008 | Store / cleaners room | Storage | 30 | 0 | 0 | 0 | 0 | 0 | 0 | No | 1 | 1 | 0 | 0 |  | Usually no exit sign unless part of escape path; check if room is windowless/occupied and local code requirement. | To check
A | G | A-009 | Reception / first aid point | Reception / First aid | 80 | 0 | 0 | 0 | 0 | 0 | 0 | No | 1 | 1 | 0 | 0 |  | Check visibility of safety equipment and escape path. Normal lighting lux is separate from emergency lighting. | To check
A | G | A-010 | External exit discharge / covered path | External egress | 50 | 1 | 0 | 0 | 0 | 0 | 0 | No | 1 | 1 | 1 | 1 |  | If part of required escape route/discharge path, coordinate with NZBC F6/F8 requirements. | To check
A | 1 | A-101 | Upper corridor | Corridor | 100 | 0 | 2 | 1 | 0 | 0 | 0 | No | 3 | 3 | 0 | 0 |  | EM within 2 m of intersections and direction changes; check spacing table between fittings. | To check
A | 1 | A-102 | Meeting / classroom / office | Room | 180 | 0 | 0 | 0 | 0 | 0 | 1 | No | 1 | 1 | 0 | 0 |  | If room forms designated area or escape route, emergency lighting required. Otherwise confirm with NZBC fire report. | To check
A | 1 | A-103 | Secondary exit lobby | Exit lobby | 70 | 2 | 0 | 0 | 0 | 0 | 0 | No | 2 | 2 | 2 | 2 |  | Exit signs at required exits; EM within 2 m approach side. | To check
TOTAL |  |  |  |  | 1215 | 7 | 4 | 2 | 0 | 8 | 2 |  | 27 | 27 | 7 | 7

## Building B
Building B – emergency lighting room/area take-off
Replace example room numbers/areas with the actual plan. Formula is a conservative planning estimate; final design must be verified against AS/NZS 2293.1 spacing tables or illuminance calculation.
Building | Level | Room/Area No. | Room/Area name | Area type | Area m² | Exit-sign doorways | Corridor intersections | Direction changes | Floor level changes | Stair/landing points requiring calc | Spacing/calc extra lights | Dual-function exit sign used? | Min emergency lights by formula | Proposed emergency lights | Exit signs required | Proposed exit signs | Fitting IDs / labels | Mounting / location notes | Compliance status | Designer notes
B | G | B-001 | Main entrance / lobby | Lobby | 120 | 2 | 0 | 0 | 0 | 0 | 0 | No | 2 | 2 | 2 | 2 |  | Exit sign at each required exit door. EM within 2 m approach side. | To check | Update with real plan room number.
B | G | B-002 | Main corridor | Corridor | 90 | 0 | 2 | 1 | 0 | 0 | 0 | No | 3 | 3 | 0 | 0 |  | EM within 2 m of intersections and direction changes; check spacing table between fittings. | To check
B | G | B-003 | Stair 1 | Stair | 35 | 1 | 0 | 0 | 0 | 4 | 0 | No | 5 | 5 | 1 | 1 |  | Use 1 lx Appendix F / calculation for each landing and tread. Position to avoid glare. | To check
B | G | B-004 | Stair 2 | Stair | 35 | 1 | 0 | 0 | 0 | 4 | 0 | No | 5 | 5 | 1 | 1 |  | Use 1 lx Appendix F / calculation for each landing and tread. Position to avoid glare. | To check
B | G | B-005 | Open office / work area | Office | 320 | 0 | 0 | 0 | 0 | 0 | 1 | No | 1 | 1 | 0 | 0 |  | At least by area allowance; add fittings using spacing table for selected classification. | To check
B | G | B-006 | Plant / switchboard room | Plant room | 60 | 0 | 0 | 0 | 0 | 0 | 0 | No | 1 | 1 | 0 | 0 |  | Provide emergency lighting if part of designated route or required by fire/maintenance strategy. | To check
B | G | B-007 | Toilets / amenities | Toilets | 45 | 0 | 0 | 0 | 0 | 0 | 0 | No | 1 | 1 | 0 | 0 |  | Emergency coverage needed if designated area or internal path of travel. | To check
B | G | B-008 | Store / cleaners room | Storage | 30 | 0 | 0 | 0 | 0 | 0 | 0 | No | 1 | 1 | 0 | 0 |  | Usually no exit sign unless part of escape path; check if room is windowless/occupied and local code requirement. | To check
B | G | B-009 | Reception / first aid point | Reception / First aid | 80 | 0 | 0 | 0 | 0 | 0 | 0 | No | 1 | 1 | 0 | 0 |  | Check visibility of safety equipment and escape path. Normal lighting lux is separate from emergency lighting. | To check
B | G | B-010 | External exit discharge / covered path | External egress | 50 | 1 | 0 | 0 | 0 | 0 | 0 | No | 1 | 1 | 1 | 1 |  | If part of required escape route/discharge path, coordinate with NZBC F6/F8 requirements. | To check
B | 1 | B-101 | Upper corridor | Corridor | 100 | 0 | 2 | 1 | 0 | 0 | 0 | No | 3 | 3 | 0 | 0 |  | EM within 2 m of intersections and direction changes; check spacing table between fittings. | To check
B | 1 | B-102 | Meeting / classroom / office | Room | 180 | 0 | 0 | 0 | 0 | 0 | 1 | No | 1 | 1 | 0 | 0 |  | If room forms designated area or escape route, emergency lighting required. Otherwise confirm with NZBC fire report. | To check
B | 1 | B-103 | Secondary exit lobby | Exit lobby | 70 | 2 | 0 | 0 | 0 | 0 | 0 | No | 2 | 2 | 2 | 2 |  | Exit signs at required exits; EM within 2 m approach side. | To check
TOTAL |  |  |  |  | 1215 | 7 | 4 | 2 | 0 | 8 | 2 |  | 27 | 27 | 7 | 7

## Take-off Summary
Emergency Lighting Take-off Summary
Building | Required emergency lights | Proposed emergency lights | Required exit signs | Proposed exit signs | Rooms/areas listed | Rows needing design/check | Notes
Building A | 27 | 27 | 7 | 7 | 13 | 13 | From Building A sheet
Building B | 27 | 27 | 7 | 7 | 13 | 13 | From Building B sheet
TOTAL | 54 | 54 | 14 | 14 | 26 | 26
Design notes / warnings
1 | The totals are planning estimates only. Final design must use actual room geometry and selected fitting photometric classification/spacing tables.
2 | For corridors, count each exit-sign door, intersection, change of direction, and low side of level change. Then check maximum spacing between fittings.
3 | For stairs, do a separate stair calculation to prove 1 lx over treads and landings. The sheet includes a count column but final luminaire positions must be checked.
4 | If a dual-function exit sign is used, it can count as both exit sign and emergency luminaire only if the product conforms and is classified for that use.
5 | Exit sign quantities depend on NZBC F8/AS1/fire report requirements and sightlines; update after checking actual egress paths.
6 | Replace example room numbers with actual room numbers from Building A and Building B drawings.

## Maintenance
Emergency lighting maintenance checklist
Frequency | Item | Activity | Record required | Applies to | Standard reference | Status
6-monthly | Emergency luminaires and exit/directional signs | Inspect each fitting/sign; record if functioning as required. | Pass/Fail per item | Both buildings | AS/NZS 2293.2:2019 Table A2 Item 2.1 | To do
6-monthly | Condition | Check free from damage, deterioration, contamination or other conditions affecting function. | Pass/Fail / noted, replaced, cleaned | Both buildings | AS/NZS 2293.2:2019 Table A2 Item 2.2 | To do
6-monthly | Exit/directional signs | Confirm direction to required exit is correct per approved design. | Pass/Fail per item | Both buildings | AS/NZS 2293.2:2019 Table A2 Item 2.3 | To do
6-monthly | Duration test | Initiate test by simulating loss of primary power using designated test facility; inspect for required duration. | Start time and Pass/Fail per fitting | Both buildings | AS/NZS 2293.2:2019 Table A2 Items 2.7–2.8 | To do
Yearly | Reflecting surfaces for indirect systems | Inspect ceilings/walls for changes that could affect approved design. | Pass/Fail | If indirect lighting used | AS/NZS 2293.2:2019 Table A4 Item 4.2 | To do
Yearly | Directional beam luminaires | Check aim is according to approved design and not directed into occupants’ eyes. | Pass/Fail per directional beam | If directional beam used | AS/NZS 2293.2:2019 Table A4 Item 4.3 | To do
Yearly | Emergency light and exit sign schedule | Check fitting schedule/drawings against installed fittings and changes since last service. | Record outcomes | Both buildings | AS/NZS 2293.2:2019 Table A4 Item 4.9 | To do
Yearly | Survey emergency luminaires | Inspect building for adequate emergency lighting according to approved design. | Pass/Fail | Both buildings | AS/NZS 2293.2:2019 Table A4 Item 4.11 | To do
Yearly | Survey exit and directional signs | Check adequate identification of exits and paths of travel to exits; check unauthorized changes. | Pass/Fail | Both buildings | AS/NZS 2293.2:2019 Table A4 Item 4.12 | To do
Records | Routine service records | Log service at the time and provide records to responsible entity before leaving or within one week. | Service record retained | Both buildings | AS/NZS 2293.2:2019 Cl 2.7 | To do
Records | Retention | Keep records on premises electronically/logbook/printed securely. | Minimum 7 years | Both buildings | AS/NZS 2293.2:2019 Cl 2.7.4 | To do

## References
References used in this workbook
Source | Section / Clause | Used for | Notes | File in workspace
AS/NZS 2293.1:2018 Incorporating Amendment No. 1 | Section 1.1, 2.2, 2.3, 2.5, 4.3–4.8, 5.2–5.8 | Design, installation, required locations, duration, exit signs | NZBC takes precedence in NZ; F6/AS1 and F8/AS1 cite AS/NZS 2293.1 as means of compliance. | /mnt/data/ASNZS-2293-12018.pdf and /mnt/data/ASNZS-2293-12018-A1.pdf
AS/NZS 2293.2:2019 | Section 2, Appendix A | Routine service, testing, record keeping, maintenance checklist | Use for ongoing compliance after installation. | /mnt/data/ASNZS-2293-22019.pdf
AS/NZS 2293.3:2018 Incorporating Amendment No. 1 | Sections 2–5, Appendices C/D | Product conformance, classification, batteries/chargers, exit sign requirements | Selected products need test data/classification. | /mnt/data/ASNZS-2293-32018.pdf and /mnt/data/ASNZS-2293-32018-A1.pdf
AS/NZS 1680.1:2006 and AS/NZS 1680 series | General interior lighting and safe movement references | Normal lighting/lux is separate from emergency lighting, but helps distinguish normal lighting design from emergency design. | Emergency lighting uses AS/NZS 2293; normal lighting uses AS/NZS 1680. | /mnt/data/ASNZS-1680-12006.pdf etc.