## Building A
Building A — Lighting Place Schedule
Floor | Room No. | Place | Task / Area Type | Workplane Height (m) | Target Maintained lx | Initial Target lx (MF 0.8) | g1 Uniformity Target | UGR Restriction (Max) | Glare / Design Notes | AS/NZS 1680 Reference | Measurement Note | Existing Luminaire (1) | Existing Qty | Existing W each | Existing Luminaire (2) | Existing Qty | Existing W each | Existing Total W | Existing Illuminance (lx) | Uniformity (Uo) | Glare (UGGR) | Proposed Luminaire | Proposed Qty | Proposed W each | Proposed Total W | Estimated Saving W | Status
Ground | 101 | Stairs | Stairs / circulation | 0 | 80 | 100 | ≥ 0.3 along route | No specific UGR; control glare | Control glare; light stair treads evenly | AS/NZS 1680.2.1 internal stairs | Measure on stair tread/floor path | Philips 2x36W | 1 | 72 |  |  |  | 72 | Slope: 267 Flat: 226 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 102 | Corridor / Lobby | Corridor / passageway / lobby | 0 | 40 | 50 | ≥ 0.3 along route | No specific UGR; control glare | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Philips 2x36W | 2 | 72 | Philips 4x36W SLB | 5 | 144 | 288 | 503 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 103 | Toilet | Toilet / amenities | 0 | 80 | 100 | ≥ 0.3–0.5 | ≤ 22 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Philips 2x36W | 1 | 72 |  |  |  | 72 | 209 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 104 | Toilet | Toilet / amenities | 0 | 80 | 100 | ≥ 0.3–0.5 | ≤ 22 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Philips 2x36W | 1 | 72 |  |  |  | 72 | 209 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 105 | Toilet Disabled | Toilet / accessible amenities | 0 | 80 | 100 | ≥ 0.3–0.5 | ≤ 22 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Philips 2x36W | 1 | 72 |  |  |  | 72 | 183 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 106 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 4x36W SLB | 2 | 144 |  |  |  | 288 | 625 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 107 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 4x36W SLB | 2 | 144 |  |  |  | 288 | 644 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 108 | Corridor | Corridor / passageway | 0 | 40 | 50 | ≥ 0.3 along route | No specific UGR; control glare | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Philips 2x36W | 4 | 72 | Philips 4x36W SLB | 4 | 144 | 432 | 373 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 109 | Mail | Office / mail task area | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 4x36W SLB | 2 | 144 |  |  |  | 288 | 615 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 110 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 4x36W SLB | 4 | 144 |  |  |  | 576 | 836 |  |  | LED low-glare panel |  |  | #REF! | #REF! | To be assessed
Ground | 111 | CAD | CAD / screen-based office work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 4x36W SLB | 4 | 144 |  |  |  | 576 | 743 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 112 | CAD | CAD / screen-based office work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 4x36W SLB | 6 | 144 |  |  |  | 864 | 1088 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 113 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 4x36W SLB | 3 | 144 |  |  |  | 432 | 743 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 114 | Visitors | Office / visitors / meeting | 0.7 | 160 | 200 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 4x36W SLB | 3 | 144 |  |  |  | 432 | 954 |  |  | LED low-glare panel |  |  |  |  | To be assessed
First | 201A | Stairs | Stairs / circulation | 0 | 80 | 100 | ≥ 0.3 along route | No specific UGR; control glare | Control glare; light stair treads evenly | AS/NZS 1680.2.1 internal stairs | Measure on stair tread/floor path | Philips 2x36W | 1 | 72 |  |  |  | 72 | 150 |  |  | LED batten / linear |  |  |  |  | To be assessed
First | 202 | Corridor | Corridor / passageway | 0 | 40 | 50 | ≥ 0.3 along route | No specific UGR; control glare | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Philips 2x36W | 4 | 72 |  |  |  | 288 | 140 |  |  | LED batten / linear |  |  |  |  | To be assessed
First | 203 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 2 | 144 |  |  |  | 288 | 331 |  |  | LED low-glare panel |  |  |  |  | To be assessed
First | 204 | Manager | Manager office | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 7 | 144 |  |  |  | 1008 | 470 |  |  | LED low-glare panel |  |  |  |  | To be assessed
First | 205 | Balcony | Balcony / circulation | 0 | 40 | 50 | ≥ 0.3 along route | No specific UGR; control glare | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Philips 2x36W | 1 | 72 |  |  |  | 72 | 181 |  |  | LED batten / linear |  |  |  |  | To be assessed
First | 206 | Toilet | Toilet / amenities | 0 | 80 | 100 | ≥ 0.3–0.5 | ≤ 22 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Philips 2x36W | 2 | 72 |  |  |  | 144 | 269 |  |  | LED batten / linear |  |  |  |  | To be assessed
First | 207 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 6 | 144 |  |  |  | 864 | 516 |  |  | LED low-glare panel |  |  |  |  | To be assessed
First | 208 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 4 | 144 |  |  |  | 576 | 458 |  |  | LED low-glare panel |  |  |  |  | To be assessed
First | 209 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 4 | 144 |  |  |  | 576 | 422 |  |  | LED low-glare panel |  |  |  |  | To be assessed
First | 210 | CAD | CAD / screen-based office work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 8 | 144 |  |  |  | 1152 | 455 |  |  | LED low-glare panel |  |  |  |  | To be assessed
First | 211 | Corridor | Corridor / passageway | 0 | 40 | 50 | ≥ 0.3 along route | No specific UGR; control glare | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Philips 2x36W | 8 | 72 |  |  |  | 576 | 133 |  |  | LED batten / linear |  |  |  |  | To be assessed
First | 212 | Common | Common office / collaboration | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 8 | 144 |  |  |  | 1152 | 435 |  |  | LED low-glare panel |  |  |  |  | To be assessed
First | 213 | Balcony | Balcony / circulation | 0 | 40 | 50 | ≥ 0.3 along route | No specific UGR; control glare | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Philips 2x36W | 1 | 72 |  |  |  | 72 | 118 |  |  | LED batten / linear |  |  |  |  | To be assessed
First | 214 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 4 | 144 |  |  |  | 576 | 416 |  |  | LED low-glare panel |  |  |  |  | To be assessed
First | 215 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 4 | 144 |  |  |  | 576 | 419 |  |  | LED low-glare panel |  |  |  |  | To be assessed
First | 216 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 4 | 144 |  |  |  | 576 | 400 |  |  | LED low-glare panel |  |  |  |  | To be assessed
First | 217 | Toilet | Toilet / amenities | 0 | 80 | 100 | ≥ 0.3–0.5 | ≤ 22 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Philips 2x36W | 1 | 72 |  |  |  | 72 | 140 |  |  | LED batten / linear |  |  |  |  | To be assessed
First | 218 | Toilet | Toilet / amenities | 0 | 80 | 100 | ≥ 0.3–0.5 | ≤ 22 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Philips 2x36W | 1 | 72 |  |  |  | 72 | 140 |  |  | LED batten / linear |  |  |  |  | To be assessed
First | 219 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 3 | 144 |  |  |  | 432 | 405 |  |  | LED low-glare panel |  |  |  |  | To be assessed
First | 220 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 4 | 144 |  |  |  | 576 | 392 |  |  | LED low-glare panel |  |  |  |  | To be assessed

## Building B
Building B — Lighting Place Schedule
Floor | Room No. | Place | Task / Area Type | Workplane Height (m) | Target Maintained lx | Initial Target lx (MF 0.8) | g1 Uniformity Target | UGR Restriction (Max) | Glare / Design Notes | AS/NZS 1680 Reference | Measurement Note | Existing Luminaire | Existing Qty | Existing W | Existing Luminaire (2) | Existing Qty (2) | Existing W (2) | Existing Total W | Existing Illuminance (lx) | Uniformity (Uo) in x-direction (g1) | Glare (UGGR) | Proposed Luminaire | Proposed Qty | Proposed W each | Proposed Total W | Estimated Saving W | Status
Ground | 101 | Stairs | Stairs / circulation | 0 | 80 | 100 | ≥ 0.3 along route | No specific UGR; control glare | Control glare; light stair treads evenly | AS/NZS 1680.2.1 internal stairs | Measure on stair tread/floor path | Philips 2x36W | 1 | 72 | Philips 4x36W SLB | 0 | 0 | 72 | Slope: 181 Flat: 237 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 102 | Corridor | Corridor / passageway | 0 | 40 | 50 | ≥ 0.3 along route | No specific UGR; control glare | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Philips 2x36W | 2 | 144 | Philips 4x36W SLB | 5 | 720 | 864 | 380 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 103 | Storage | Storage / occasional use | 0 | 40 | 50 | ≥ 0.3–0.5 | ≤ 25 | Enough light for safe access | AS/NZS 1680.2.1 comparable storage/movement | Use 40 lx only if rarely entered; 80 lx safer | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 1 | 144 | 144 | 325 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 104 | Utility | Utility / cleaner room | 0 | 80 | 100 | ≥ 0.3–0.5 | ≤ 25 | Avoid glare; allow safe use of equipment | AS/NZS 1680.2.1 comparable utility area | Use 0.7 m if detailed work is done | Philips 2x36W | 1 | 72 | Philips 4x36W SLB | 0 | 0 | 72 | 205 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 105 | Toilet | Toilet / amenities | 0 | 80 | 100 | ≥ 0.3–0.5 | ≤ 22 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Philips 2x36W | 1 | 72 | Philips 4x36W SLB | 0 | 0 | 72 | 201 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 106 | Toilet | Toilet / amenities | 0 | 80 | 100 | ≥ 0.3–0.5 | ≤ 22 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Philips 2x36W | 1 | 72 | Philips 4x36W SLB | 0 | 0 | 72 | 186 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 107 | Shower | Shower / amenities | 0 | 160 | 200 | ≥ 0.3–0.5 | ≤ 22 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Philips 2x36W | 1 | 72 | Philips 4x36W SLB | 0 | 0 | 72 | 187 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 108 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 4 | 576 | 576 | 753 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 109 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 2 | 288 | 288 | 801 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 110 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 6 | 864 | 864 | 1107 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 111 | Manager | Manager office | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 2 | 288 | 288 | 740 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 112 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 3 | 432 | 432 | 865 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 113 | Corridor / Coffee | Corridor / coffee area | 0 | 40 | 50 | ≥ 0.3 along route | No specific UGR; control glare | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 2 | 288 | 288 | 403 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 114 | Storage | Storage / occasional use | 0 | 40 | 50 | ≥ 0.3–0.5 | ≤ 25 | Enough light for safe access | AS/NZS 1680.2.1 comparable storage/movement | Use 40 lx only if rarely entered; 80 lx safer | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 1 | 144 | 144 | 403 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 115 | Reception | Reception / enquiry desk | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Good facial visibility; low glare | AS/NZS 1680.1 enquiry desks / office tasks | Desk/counter task plane | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 4 | 576 | 576 | 1069 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 116 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 2 | 288 | 288 | 854 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 117 | Corridor | Corridor / passageway | 0 | 40 | 50 | ≥ 0.3 along route | No specific UGR; control glare | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 6 | 864 | 864 | 538 |  |  | LED batten / linear |  |  |  |  | To be assessed
Ground | 118 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 4 | 576 | 576 | 1064 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 119 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 1 | 144 | 144 | 538 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 120 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 4 | 576 | 576 | 1133 |  |  | LED low-glare panel |  |  |  |  | To be assessed
Ground | 121 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 2 | 288 | 288 | 900 |  |  | LED low-glare panel |  |  |  |  | To be assessed
First | 201 | Stairs | Stairs / circulation | 0 | 80 | 100 | ≥ 0.3 along route | No specific UGR; control glare | Control glare; light stair treads evenly | AS/NZS 1680.2.1 internal stairs | Measure on stair tread/floor path | Philips 2x36W | 1 | 72 | Philips 4x36W SLB | 0 | 0 | 72 | 229 | 0.93 |  | LED batten / linear |  |  |  |  | To be assessed
First | 202 | Corridor | Corridor / passageway | 0 | 40 | 50 | ≥ 0.3 along route | No specific UGR; control glare | Avoid dark patches and glare | AS/NZS 1680.2.1 corridors / circulation | Floor-level calculation plane | Philips 2x36W | 2 | 144 | Philips 4x36W SLB | 0 | 0 | 144 | 168 | 0.07 |  | LED batten / linear |  |  |  |  | To be assessed
First | 203A | DB | Electrical DB / utility | 0 | 80 | 100 | ≥ 0.3–0.5 | ≤ 25 | Avoid glare; allow safe use of equipment | AS/NZS 1680.2.1 comparable utility area | Use 0.7 m if detailed work is done | Philips 2x36W | 0 | 0 | Philips 4x36W SLB | 0 | 0 | 0 | 0 | 0 |  | LED batten / linear |  |  |  |  | To be assessed
First | 203 | Director | Director office | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 4 | 288 | Philips 4x36W SLB | 0 | 0 | 288 | 291 | 0.67 | 22 | LED low-glare panel |  |  |  |  | To be assessed
First | 204 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 4 | 288 | Philips 4x36W SLB | 0 | 0 | 288 | 384 | 0.77 | 20.8 | LED low-glare panel |  |  |  |  | To be assessed
First | 205 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 5 | 360 | Philips 4x36W SLB | 0 | 0 | 360 | 375 | 0.59 | 22.6 | LED low-glare panel |  |  |  |  | To be assessed
First | 206 | Kitchen | Kitchen / kitchenette | 0.85 | 160 | 200 | ≥ 0.5 | ≤ 22 | Good bench visibility; avoid glare | AS/NZS 1680.2.1 kitchen general | Use 240 lx at food prep/washing-up benches | Philips 2x36W | 7 | 504 | Philips 4x36W SLB | 0 | 0 | 504 | 316 | 0.62 | 25.1 | LED batten / linear |  |  |  |  | To be assessed
First | 207 | Office (CAD) | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 9 | 648 | Philips 4x36W SLB | 0 | 0 | 648 | 476 | 0.66 | 21.4 | LED low-glare panel |  |  |  |  | To be assessed
First | 208 | Meeting | Meeting room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 6 | 432 | Philips 4x36W SLB | 0 | 0 | 432 | 552 | 0.72 | 18.5 | LED low-glare panel |  |  |  |  | To be assessed
First | 209 | Toilet | Toilet / amenities | 0 | 80 | 100 | ≥ 0.3–0.5 | ≤ 22 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Philips 2x36W | 2 | 144 | Philips 4x36W SLB | 0 | 0 | 144 | 227 | 0.87 | 17.5 | LED batten / linear |  |  |  |  | To be assessed
First | 210 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 9 | 648 | Philips 4x36W SLB | 0 | 0 | 648 | 676 | 0.68 | 21.5 | LED low-glare panel |  |  |  |  | To be assessed
First | 211 | Toilet | Toilet / amenities | 0 | 80 | 100 | ≥ 0.3–0.5 | ≤ 22 | Comfortable general lighting; use IP-rated luminaire in wet areas | AS/NZS 1680 comparable amenities | Practical target for office amenities | Philips 2x36W | 3 | 216 | Philips 4x36W SLB | 0 | 0 | 216 | 273 | 0.66 | 21.1 | LED batten / linear |  |  |  |  | To be assessed
First | 212 | Office | Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare, screen reflection control, CRI ≥80 | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height working plane | Philips 2x36W | 8 | 576 | Philips 4x36W SLB | 0 | 0 | 576 | 622 | 0.7 | 18.7 | LED low-glare panel |  |  |  |  | To be assessed
First | 212A | DB | Electrical DB / utility | 0 | 80 | 100 | ≥ 0.3–0.5 | ≤ 25 | Avoid glare; allow safe use of equipment | AS/NZS 1680.2.1 comparable utility area | Use 0.7 m if detailed work is done | Philips 2x36W | 1 | 72 | Philips 4x36W SLB | 0 | 0 | 72 | 136 | 0.76 | 11.9 | LED batten / linear |  |  |  |  | To be assessed
First | 213 | Conference | Conference room | 0.7 | 320 | 400 | ≥ 0.7 on task area | ≤ 19 | Low glare; allow presentation/screen use | AS/NZS 1680.1 office meeting task | Use dimming if presentation mode is required | Philips 2x36W | 8 | 576 | Philips 4x36W SLB | 0 | 0 | 576 | 458 | 0.62 | 20.8 | LED low-glare panel |  |  |  |  | To be assessed

## Building B - First Floor
Floor | Room No. | Place | Task / Area Type | Workplane Height (m) | Target Maintained lx | Target Uniformity | Glare | Luminaire | Suspension | Calculated lx | Calculated Uniformity | Glare
First | 201 | Stairs | Stairs / circulation | 0 | 80 | ≥ 0.3 |  | ETAP R3111/LEDW445DX1 x 3 | 2.8m | 307 | 0.93
First | 202 | Corridor | Corridor / passageway | 0 | 40 | ≥ 0.3 |  | ETAP R3111/LEDW445DX1 x 4 | 2.8m | 199 | 0.064
First | 203A | DB | Electrical DB / utility | 0 | 80 |  |  | ETAP R3111/LEDN445DX1 x 5 | 2.8m
First | 203 | Director | Director office | 0.7 | 320 | ≥ 0.5 |  | ETAP R3111/LEDN445DX1 x 6 | 2.8m | 367 | 0.65
First | 204 | Meeting | Meeting room | 0.7 | 320 | ≥ 0.5 |  | ETAP R3111/LEDN445DX1 x 7 | 2.8m | 494 | 0.73
First | 205 | Office | Office desk / screen work | 0.7 | 320 | ≥ 0.5 |  | ETAP R3111/LEDN445DX1 x 8 | 2.8m | 481 | 0.62
First | 206 | Kitchen | Kitchen / kitchenette | 0.85 | 160 | ≥ 0.5 |  | ETAP R3111/LEDN445DX1 x 9 | 3.0m | 391 | 0.6
First | 207 | Office (CAD) | Office desk / screen work | 0.7 | 320 | ≥ 0.5 | <= 19 | ETAP R3111/LEDN445DX1 x 9 | 2.8m | 588 | 0.66 | 18.5
First | 208 | Meeting | Meeting room | 0.7 | 320 | ≥ 0.5 |  | ETAP R3111/LEDN445DX1 x 10 | 2.8m | 709 | 0.74
First | 209 | Toilet | Toilet / amenities | 0 | 80 | ≥ 0.3 |  | ETAP R3111/LEDN445DX1 x 11 | 2.8m | 296 | 0.86
First | 210 | Office | Office desk / screen work | 0.7 | 320 | ≥ 0.5 |  | ETAP R3111/LEDN445DX1 x 12 | 2.8m | 845 | 0.69
First | 211 | Toilet | Toilet / amenities | 0 | 80 | ≥ 0.3 |  | ETAP R3111/LEDN445DX1 x 13 | 2.8m | 350 | 0.69
First | 212 | Office | Office desk / screen work | 0.7 | 320 | ≥ 0.5 |  | ETAP R3111/LEDN445DX1 x 14 | 2.8m | 785 | 0.72
First | 212A | DB | Electrical DB / utility | 0 | 80 | ≥ 0.3 |  | ETAP R3111/LEDN445DX1 x 15 | 2.8m | 196 | 0.63
First | 213 | Conference | Conference room | 0.7 | 320 | ≥ 0.5 |  | ETAP R3111/LEDN445DX1 x 16 | 2.8m | 569 | 0.93

## Reference
AS/NZS 1680 quick reference used in schedules
Space / task | Workplane height (m) | Maintained lux | Initial lux target (MF 0.8) | g1 uniformity | Glare note | Reference basis | Measurement note
Office desk / screen work | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare / UGR ≤19 preferred; control screen reflections | AS/NZS 1680.1 / 1680.2.2 office tasks | Desk-height plane
Meeting / conference | 0.7 | 320 | 400 | ≥ 0.7 on task area | Low glare; allow dimming for presentation | AS/NZS 1680.1 comparable office task | Table-height plane
Reception / enquiry desk | 0.7 | 320 | 400 | ≥ 0.7 on task area | Good facial visibility; low glare | AS/NZS 1680.1 enquiry desks | Counter/desk plane
Corridor / passageway | 0 | 40 | 50 | ≥ 0.3 along route | Avoid dark patches and glare | AS/NZS 1680.2.1 circulation | Floor level
Stairs | 0 | 80 | 100 | ≥ 0.3 along route | Light treads evenly | AS/NZS 1680.2.1 internal stairs | Stair tread/floor path
Storage / occasional use | 0 | 80 | 100 | ≥ 0.3–0.5 | Safe access lighting | AS/NZS 1680.2.1 comparable storage | Floor level
Utility / DB | 0 | 80 | 100 | ≥ 0.3–0.5 | Safe equipment access | AS/NZS 1680 comparable utility | Use actual task plane if needed
Toilet / WC / shower | 0 | 160 | 200 | ≥ 0.3–0.5 | Comfortable general lighting; IP-rated in wet areas | AS/NZS 1680 comparable amenities | Floor level
Kitchen general | 0.85 | 160 | 200 | ≥ 0.5 | Bench visibility | AS/NZS 1680.2.1 kitchen general | Bench height
Food prep / washing up | 0.85 | 240 | 300 | ≥ 0.7 on task area | Control glare on wet surfaces | AS/NZS 1680.2.1 food preparation | Bench height